## Slide 1: Techno-Commercial Offer
Authorised Signatory
Checked By
Nilesh Gadge
Prepared By
Maulik Rathod
Environ 14-15-16 Rudraksh Complex, Opp. Annapurna Hotel ,GIDC Phase I, Vatva, Ahmedabad - 382445, Gujarat Phone No. : +91 79 40027345 | Quotation No : ENVQ8915 Quotation Date : Sales Contact Person : Nilesh Gadgi Contact No : +91 7227988038 Email : sales@environindia.net
To, Phone : +91 | Enquiry Reference No. : By Visit Enquiry Reference Date. : Email ID : Kind Attention : Mr. Mobile No. : +91
Sr. No. | Item Description | Qty | Unit | Unit Price | Total Price
1 | Manufacturing & Supply Sewage Treatment Plant Of Capacity 90 KLD Annexure I - Basis of Design Annexure II - STP process Flow diagram Annexure III - List of Equipment Annexure IV - Technical Data Sheet | 1 | Nos | Rs. 12,85,000/- | Rs. 12,85,000/-
www.environindia.net

## Slide 2: Commercial Terms
1 | Price Basis | Ex-Works ahmedabad unpacked condition. Civil work will be under client’s scope.
2 | Packing, Forwarding & Freight | Extra at actual ( Client Scope )
3 | Delivery Term | 15 - 18 weeks from the date of receipt of your valued purchase order and advance payment.
4 | Terms of Payment | 50% advance along with the order 45% including all taxes & duties shall be paid against Performa invoice prior to dispatch from our works. 5% after installation & commissioning or within three months from the date
5 | Taxes & Duties | Extra at actual at the time of dispatch
6 | Octroi & Insurance | Extra at actual at the time of dispatch
7 | Inspection | At our works prior to dispatch at your cost. The inspection shall be visual and will not include any performance or operating tests. We shall provide test certificates from the manufacturers (of important equipment only), if you like. For producing goods for inspection, we shall intimate to you when the goods are ready for shipment. You will have to get the inspection done within 4 days of our notice. If the inspecting agency fails to show up during this period, we shall presume that you have waived off the inspection clause and we shall under intimation to you ship the consignment without inspection.
8 | Installation & Commissioning | Erection charges are included in our scope. The chemical dosing which requires at commissioning &operation time will be in our scope. Required cow dung for commissioning & other like Urea, DAP; Dextrose, jiggery etc will be under our scope in quantity as we say. However, supervisory services will be provided for the commissioning of the system on the following terms & conditions. We shall depute our engineers to site for assistance of commissioning at a cost of Rs. 3000/- per persons per day (8 working hours) To & fro traveling, lodging & boarding, local traveling shall be borne by client. Skilled & unskilled labor and tools & tackles to be provided by client.
9 | Jurisdiction | In the unlikely event of a dispute relating to supplied product, dispute shall be subjected to the jurisdiction of Ahmedabad (India) courts.
10 | Validity | Our Quotation will be valid for your kind consideration for a period of 30 days from the date hereof. Any extension thereafter will be subject to our written confirmation only.
11 | Exclusions | M/s. Environ, Ahmadabad shall undertake the assignment with following exclusions: 1. Collection tank with slab on top for keeping plant. Two Man hole of 400 x 400 mm to be provided on slab. 2. Incoming waste water up to raw transfer pumps. 3. Treated water storage tank. 4. Chemicals required for plant operation up to the dosing tank. 5. Supply/ laying and termination of incoming power cables up to local electrical panel. 6. Any emergency/ critical power supply. 7. Any other studies or modification of the scope shall be carried out with extra costs. 8. Liaison work (if any) will not be in scope of Environ 9. Safety and security by client. 10. All statutorily Government approvals, if any.
www.environgindia.net

## Slide 3
ANNEXURE - I
Daily Flow (Maximum) | 90 m3/Day
PH | 6-8
COD | 400mg/l
BOD | 300mg/l
TSS | 200 mg/l
Untreated Sewage Parameters (Assumed)
Treated Sewage Quality
PH | 7-7.5
COD | <250 mg/l
BOD | <100 mg/l
TSS | <20mg/l
www.environgindia.net

## Slide 4
4
ANNEXURE - II
STP PROCESS FLOW DIAGRAM
www.environgindia.net
BAR SCREEN
RAW SEWAGE COLLECTION TANK
PRIMARY SETTLING TANK
AERATION TANK
SECONDARY SETTLING TANK
TREATED WATER HOLDING TANK
PRESSURE SAND FILTER
ACTIVATED CARBON FILTER
FINAL STORAGE TANK

## Slide 5
5
ANNEXURE – III
SEWAGE TREATMENT PROCESS
SCOPE OF SUPPLY – BY ENVIRON
www.environgindia.net
Sr. No | Parameter | Quantity
1 | Raw Effluent Transfer Pump | 2(1W +1S)
2 | Aeration Grid ( Diffuser) | 1 Lot
3 | Air Blowers | 2 (1W +1S)
4 | MBBR Media | 1 Lot
5 | Return Activated Sludge Transfer Pump | 2 (1W +1S)
Tertiary System |  | 
6 | Filter Feed Pump | 2 (1W +1S)
7 | Pressure Sand Filter | 1 No
8 | Activated Carbon Filter | 1 No.
9 | Control panel | As per Design
10 | Inter cabling work | As per Design
11 | Inter Connecting Piping and accessories | Std. Make
Scope of Supply – Client ( Civil) All tank’s volume is in m3 |  |  | 
1 | Collection Tank | As per Design | RCC
2 | Settling Tank | As per Design | RCC
3 | Aeration Tank | As per Design | RCC
4 | Final Holding Tank | As per Design | RCC
5 | Sludge Bed | As per Design | Brick
6 | Miscellaneous Civil Work ( Foundation ) | As per Requirement | RCC

## Slide 6
6
6
ANNEXURE – IV
TECHNICAL DATASHEET
Quantity | 1 No
Capacity ( Liquid Volume ) | As Per Design
Dimension | To Be Provided
MOC | RCC / Civil
Collection Tank
Quantity | 2 No. ( 1W + 1S )
Flow Rate | 4.5 m3 / hr.
MOC | CI
Head | 10 – 15 Meter
Speed | 1440 RPM
Type | Self Priming Non Clog Monoblock
Make | JEE / Kirloskar / Lubi / Equivalent
Raw Sewage Transfer Pump
www.environgindia.net
Quantity | 1 No.
Capacity | As Per Design
Dimension | As Per Design
MOC | RCC/CIVIL
Aeration Tank
Quantity | 2 No. ( 1W + 1S )
Type | Tri Lobe Rotary Blower
Pressure | 0.4 kg / cm2
Type Of Cooling | Air Cooling
Type Of Drive | V-Belt Drive
Frequency | 50 HZ
Air Flow | 75 m3 / Hr
Suction Temperature | Ambient
Flow Direction | Horizontal
Make Of Blower | AGS / TMVT / Shreeji Equivalent
Air Blower

## Slide 7
Quantity | 1 Lot
Type | Tubular Fine Bubble
Dimension | 63 x 1000
Operating Air Temperature | 5-80’
MOC | EPDM / Hige Grade Silicon / Equivalent
Make | Airfin / Fivbro/ Equivalent
Air Diffuser
Settling Tank
www.environgindia.net
Quantity | 1 Lot
Type | Fluidized Bio Media
Dimension | 22mm (Dia) x 1000 (16 mm height)
Color | Black
MOC | Virgin PPUV Stabilized
Density | 0.93
Temperature | 80’ C
MBBR Media
Quantity | 2 No ( 1W + 1S )
Flow Rate | 4.5 m3 / Hr
MOC | CI Base / SS Impeller
Head | 10-15 Meter
Type | Self Priming Non clog Monoblock
Make | JEE / Kirloskar / Lubi / Equilant
Raw Activated Sludge Pump
Quantity | 1 Nos
MOC | RCC/CIVIL
Dimension | AS PER DESIGN
CAPACITY | AS PER DESIGN
Holding Tank
Quantity | 2 No.
Capacity | As Per Design
Dimension | As Per Design
MOC | RCC/CIVIL

## Slide 8
8
8
www.environgindia.net
Quantity | 1 No.
Flow Rate | 4.5 m3 / Hr
MOC | FRP
Duration Of Backwash | 10 – 15 Minutes
Pressure | 2.5 Kg/cm2
Make | Pentair
Application | To Remove Suspended Solids / Undissolved Impurities
Pressure Sand Filter
Quantity | 1 No.
Flow Rate | 4.5 m3 / Hr
MOC | FRP
Duration Of Backwash | 10 – 15 Minutes
Pressure | 2.5 Kg/cm2
Make | Pentair
Top – Bottom Distribution | Strainer
Application | To Remove Suspended Solids / Undissolved Impurities
Activated Carbon Filter
Filter Feed Pump
Quantity | 2 No. ( 1W + 1S )
Flow Rate | 4.5 m3 / Hr
MOC | CI Base / SS Impeller
Head | 20 – 25 Meter
Type | Centrifugal
Make | JEE / Kirloskar/ Lubi / Equivalent
Quantity | 1 Lot
Types | UPVC / CPVC / HDPE / GI / MS, Interconnecting Piping Within Battery
Valves | Butterfly Valve, Ball Valve and Isolation Valves As Required
Supports | Pipe Supports For Interconnecting Piping And Skid
MOC | UPVC / HDPE / GI / MS
Interconnecting Piping & Valves

## Slide 9
9
9
www.environgindia.net
Electric Control Panel | MS Foot Mounted MS Powder Coating
Type | Free Standing Cubical
Contact Parts | L&T / Schneider
Wire | Copper
Control Panel