## Slide 1: Techno-Commercial Offer
Authorised Signatory
Checked By
Vishal Surati
Prepared By
Maulik Rathod
Sr. No. | Item Description | Qty | Unit | Unit Price | Total Price
1 | Manufacturing & Supply Sewage Treatment Plant Of Capacity 15 KLD ( SBR Technology ) Annexure I - Basis of Design Annexure II - Description of the treatment scheme Annexure III – Scope of supply Annexure IV - Technical Data Sheet | 1 | Nos | Rs. 6,95,000/- | Rs. 6,95,000/-
www.environindia.net
Environ 14-15-16 Rudraksh Complex, Opp. Annapurna Hotel ,GIDC Phase I, Vatva, Ahmedabad - 382445, Gujarat Phone No. : +91 79 40027345 | Quotation No : ENVQ891654 Quotation Date : 13.02.2019 Sales Contact Person : Vishal Surati Contact No : +91 8866088038 Email : sales@environindia.net
To, PLOT NO. - AV10, BOL INDUSTRIAL ESTATE,GIDC - II,SANAND, GUJARAT, Chharodi, Gujarat. Phone : +91 | Enquiry Reference No. : By Mail Enquiry Reference Date. : 12.02.2019 Email ID :ucsmiraj@gmail.com Kind Attention : Mr. Amol Patil Mobile No. : +91 9665381937

## Slide 2: Commercial Terms
1 | Price Basis | Ex-Works ahmedabad unpacked condition. Civil work will be under client’s scope.
2 | Packing, Forwarding & Freight | Extra at actual ( Client Scope )
3 | Delivery Term | 6 - 10 weeks from the date of receipt of your valued purchase order and advance payment.
4 | Terms of Payment | 50% advance along with the order 45% including all taxes & duties shall be paid against Performa invoice prior to dispatch from our works. 5% after installation & commissioning or within three months from the date
5 | Taxes & Duties | Extra at actual at the time of dispatch
6 | Inspection | At our works prior to dispatch at your cost. The inspection shall be visual and will not include any performance or operating tests. We shall provide test certificates from the manufacturers (of important equipment only), if you like. For producing goods for inspection, we shall intimate to you when the goods are ready for shipment. You will have to get the inspection done within 4 days of our notice. If the inspecting agency fails to show up during this period, we shall presume that you have waived off the inspection clause and we shall under intimation to you ship the consignment without inspection.
7 | Installation & Commissioning | Erection charges are included in our scope. The chemical dosing which requires at commissioning &operation time will be in Client scope. Required cow dung for commissioning & other like Urea, DAP; Dextrose, jiggery etc will be under client scope in quantity as we say. To & fro traveling, lodging & boarding, local traveling shall be borne by client. Skilled & unskilled labor and tools & tackles to be provided by client.
8 | Jurisdiction | In the unlikely event of a dispute relating to supplied product, dispute shall be subjected to the jurisdiction of Ahmedabad (India) courts.
9 | Validity | Our Quotation will be valid for your kind consideration for a period of 30 days from the date hereof. Any extension thereafter will be subject to our written confirmation only.
10 | Exclusions | M/s. Environ, Ahmadabad shall undertake the assignment with following exclusions: 1. Collection tank with slab on top for keeping plant. Two Man hole of 400 x 400 mm to be provided on slab. 2. Incoming waste water up to raw transfer pumps. 3. Treated water storage tank. 4. Chemicals required for plant operation up to the dosing tank. 5. Supply/ laying and termination of incoming power cables up to local electrical panel. 6. Any emergency/ critical power supply. 7. Any other studies or modification of the scope shall be carried out with extra costs. 8. Liaison work (if any) will not be in scope of Environ 9. Safety and security by client. 10. All statutorily Government approvals, if any.
www.environindia.net

## Slide 3
ANNEXURE – I
DESIGN BASES
Daily Flow (Maximum) | 15 m3/Day
COD | 350-500 mg/l
BOD | 300mg/l
TSS | 200 mg/l
Raw Water Parameters
Treated Water Parameters
COD | <100 mg/l
BOD | <30 mg/l
TSS | <30 mg/l
The quality and quantity of treated water will be based on the raw/feed water quality and quantity. Any change in raw/feed water quality and/or quantity, it will reflect in the treated water quality and/or quantity.
The treated sewage can be utilized for gardening, horticulture and/or irrigation purpose.
Environ is the pioneer in sewage treatment systems that are fully automatic, efficient and meet the treatment standards which are higher than the statutory requirements. Our treatment systems have won the confidence of many clients and every client has been testimonial to the plant performance. The choice of the electro-mechanical equipment and the meticulous design set us ahead in the market for high quality sewage treatment systems.
Fully automatic sewage treatment systems by Environ can be installed and retrofitted in the plastic or concrete container at any time.
Fully biological small wastewater treatment plant based on the SBR principle.
Single or multiple container models from 1 KLD to 500 KLD.
Energy-efficient due to fine-bubble pressure diffusion and ventilation.
Due to the compact design, Environ saves large space which is advantageousto the Real Estate Developers and promoters as more space will be available for construction, recreation and other developments.
No need for centralized plumbing as each villa can have its own STP.
Reduces operation and maintenance burden/costs for associations and Reduces electricity costs to almost 75%.
No need for a full time service person to maintain sewage tanks.
Need not evacuate sludge on a frequent mode, can be done once in a year or more.
Need not have a large room for sewage treatment plant; this can be fitted within a small underground space.
Automated maintenance system with 24/7 dashboard links to CPU, smart phones, with email and message (sms) indications.
Any emergency operations can be done through internet or mobile phone. User controls given to each users including operations or just view only.
Intelligent system with auto sleeps and holiday mode when less inflow, ideal for development where there is lesser number of people during weekdays.
Water can be reused for gardening purpose, with almost zero smell, further the water can be filtered for toilet reuse with additional simple filter units.
Treated Water Parameters
www.environindia.net

## Slide 4
4
ANNEXURE - II
DISCRIPTION OF THE TREATMENT SCHEME
This system contain only two tanks which includes total four phases in the whole operation cycle. The four phase operation cycle is described below;
Loading Phase
The wastewater is initially fed into the sludge tank (1stchamber) where solid constituents are removed. From here, the wastewater is then gradually led into the SBR tank (2nd Chamber).
Aeration Phase
The SBR tank is where the actual biological treatment process takes place. Here, short aeration and rest phases alternate with one another within the scope of a controlled cleaning process. This means that the so-called activated sludge with its millions of micro-organisms can develop and treat the water thoroughly.
Rest Phase
During the 90 minute rest phase, the activated sludge then settles on the bottom of the tank. A clear water zone forms on the upper part of the SBR tank.
Clearwater Extraction
The separated clear water is then led from the SBR tank to the receiving water (stream, river or lake) or into a percolation system. Afterwards, the sludge is returned to the first chamber from the SBR tank and the process starts again from the beginning.
www.environindia.net

## Slide 5
5
ANNEXURE – III
SEWAGE TREATMENT PLANT
Sr. No | Name of Units/Items | Quantity
ENVIRON SBR Unit for 15 m3/day |  | 
1 | For Retrofitting The Following New Sewage Pits: The Plant Will Be Retrofitted In The Tanks | 1 No.
2 | The Two Chamber Pit Consists Of : Mounting Parts; Charging Air Lifter Clear Water Air Lifter Excessive Air Sludge Lifter | 2 No.
3 | ENVIRON - Hose Set Membrane Air Diffuser (Finely Perforated EPDM) Stainless Steel Air Supply System | 1 Lot
4 | Fixing Material Machine Technology For Indoor Installation, In A Cool, Dry And Dust-free Environment 1 No. Compressor Rotary Vane Compressor (1 Kw, 220v, 1 ~) 1 No. With Microprocessor Control With Preset Work Cycles, Real-time Controlled, Graphic Display, 14 Operating Keys, Operating Hours Counter, Optional Manual And Automatic Mode 3 Operating Levels, (Operator, Service, Manufacturer) | 1 Lot
SCOPE OF SUPPLY – BY ENVIRON
DETAILS OF THE CIVIL UNITS (CLIENT’S SCOPE)
Sr. No | Name of Units | Volume (m3)* | MOC
1 | Primary Tank | As per Design | RCC
2 | Sequential Batch Reactor | As per Design | RCC
3 | Treated Water Tank (If Required) | As per Design | RCC
4 | Miscellaneous Civil Work (Piping Network) | As Per Requirement | RCC
Above volumes are liquid volumes only. Exact dimensions of the units will be provided in detailed design drawings in future. The above tank volume will depend on water depth. Water depth should be 2.5m. If it is changed than dimension will be changed. |  |  | 
www.environindia.net

## Slide 6
6
ANNEXURE – III
SEWAGE TREATMENT PLANT
www.environindia.net
Quantity | 2 No. ( 1W + 1S )
Flow Rate | 0.75 m3 / Hr
MOC | CI Base / SS Shaft & Bronze / SS Impeller
Head | 10 – 15 Meter
Type | Centrifugal, Mono Block
Make | Kirloskar / Lubi / Indoforce/ Equivalent
Filter Feed Pump
Quantity | 1 No.
Flow Rate | 0.75m3 / Hr
MOC | FRP
Duration Of Backwash | 10 – 15 Minutes
Pressure | 2.5 Kg/cm2
Make | Pentair
Application | To Remove Suspended Solids / Undissolved Impurities
Pressure Sand Filter
Quantity | 1 No.
Flow Rate | 0.75m3 / Hr
MOC | FRP
Duration Of Backwash | 10 – 15 Minutes
Pressure | 2.5 Kg/cm2
Make | Pentair
Top – Bottom Distribution | Strainer
Application | To Remove Suspended Solids / Undissolved Impurities
Activated Carbon Filter
Quantity | 1 Lot
Types | UPVC / CPVC / HDPE / GI / MS, As Applicable Complete Interconnecting Piping Within Battery
Valves | Butterfly Valve, Ball Valve and Isolation Valves As Required
Supports | Pipe Supports For Interconnecting Piping And Skid
MOC | UPVC / HDPE / GI / MS
Interconnecting Piping & Valves